- Section 08 71 00 - Door Hardware

  - PART 1  GENERAL

    - ADMINISTRATIVE REQUIREMENTS

      - Coordinate the manufacture, fabrication, and installation of products that door hardware is installed on.

      - Sequence installation to ensure utility connections are achieved in an orderly and expeditious manner.

      - Furnish templates for door and frame preparation to manufacturers and fabricators of products requiring internal reinforcement for door hardware.

      - Keying Requirements Meeting:

        - Schedule meeting at project site prior to Contractor occupancy.

        - Attendance Required:

          - Contractor.

          - Owner.

        - Agenda:

          - Establish keying requirements.

          - Verify locksets and locking hardware are functionally correct for project requirements.

        - Incorporate "Keying Requirements Meeting" decisions into keying submittal upon review of door hardware keying system including, but not limited to, the following:

          - Access control requirements.

        - Deliver established keying requirements to manufacturers.

    - SUBMITTALS

      - Product Data:  Manufacturer's catalog literature for each type of hardware, marked to clearly show products to be furnished for this project, and includes construction details, material descriptions, finishes, and dimensions and profiles of individual components.

      - Shop Drawings - Door Hardware Schedule:  Submit detailed listing that includes each item of hardware to be installed on each door. Use door numbering scheme as included in Contract Documents.

        - Prepared by or under supervision of Architectural Hardware Consultant (AHC).

        - Provide complete description for each door listed.

  - PART 2  PRODUCTS

    - DESIGN AND PERFORMANCE CRITERIA

      - Provide specified door hardware as required to make doors fully functional, compliant with applicable codes, and secure to extent indicated.

      - Provide individual items of single type, of same model, and by same manufacturer.

      - Provide door hardware products that comply with the following requirements:

        - Applicable provisions of federal, state, and local codes.

        - Accessibility:  ADA Standards and ICC A117.1.

        - Fire-Rated Doors:  NFPA 80, listed and labeled by qualified testing agency for fire protection ratings indicated, based on testing at positive pressure in accordance with NFPA 252 or UL 10C.

        - Hardware on Fire-Rated Doors:  Listed and classified by ​UL (DIR), ITS (DIR), or testing firm acceptable to authorities having jurisdiction​ as suitable for application indicated.

        - Listed and certified compliant with specified standards by BHMA (CPD).

        - Products Requiring Electrical Connection:  Listed and classified by UL (DIR) as suitable for the purpose specified.

      - Electrically Operated and/or Controlled Hardware:  Provide necessary power supplies, power transfer hinges, relays, and interfaces as required for proper operation; provide wiring between hardware and control components and to building power connection in compliance with NFPA 70.

      - Lock Function:  Provide lock and latch function numbers and descriptions of manufacturer's series. Refer to ​Door Hardware Schedule​.

      - Fasteners:

        - Provide fasteners of proper type, size, quantity, and finish that comply with commercially recognized standards for proposed applications.

          - Aluminum fasteners are not permitted.

          - Provide phillips flat-head screws with heads finished to match door surface hardware unless otherwise indicated.

        - Fire-Rated Applications:  Comply with NFPA 80.

          - Provide wood or machine screws for hinges mortised to doors or frames, strike plates to frames, and closers to doors and frames.

          - Provide steel through bolts for attachment of surface mounted closers, hinges, or exit devices to door panels unless proper door blocking is provided.

    - HINGES

      - Hinges:  Comply with BHMA A156.1, Grade 1.

        - Provide hinges on every swinging door.

        - Provide following quantity of butt hinges for each door:

          - Doors up to 60 inches High:  Two hinges.

          - Doors From 60 inches High up to 90 inches High:  Three hinges.

| HINGE TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | BUTT HINGES, FULL MORTISE, 5-KNUCKLE, BALL BEARING, STANDARD WEIGHT, GRADE 1, 4.5X4.5 | 626 (NON-RATED),652 (RATED) |
| A | SAME AS X, WITH NON-REMOVABLE PIN | 626 (NON-RATED),652 (RATED) |

    - FLUSH BOLTS

      - Flush Bolts:  Comply with BHMA A156.16, Grade 1.

        - Flush Bolt Throw:  3/4 inch, minimum.

        - Provide dustproof floor strike for bolt into floor, except at metal thresholds.

| FLUSH BOLT TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | MANUAL FLUSH BOLT SET (TOP & BOTTOM) | 626 |
| A | AUTOMATIC FLUSH BOLT SET (TOP & BOTTOM) | 626 |
| B | DUST-PROOF STRIKE | 626 |

    - EXIT DEVICES

      - Exit Devices:  Comply with BHMA A156.3, Grade 1.

        - Lever design to match lockset trim.

        - Provide cylinder with cylinder dogging or locking trim.

        - Provide exit devices properly sized for door width and height.

        - Provide strike as recommended by manufacturer for application indicated.

        - Provide UL (DIR) listed exit device assemblies for fire-rated doors and panic device assemblies for non-fire-rated doors.

      - Functions and types are indicated in the “notes” column of the hardware set schedule.

      - For two-leaf doors, provide a panic/exit device on both leaves where “(2)” is indicated in the hardware set schedule.

| PANIC/EXIT DEVICE TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | EXIT DEVICE, GRADE 1 | 626 (NON-RATED),652 (RATED) |

    - LOCK AND LATCH SETS

      - Functions are indicated in the “notes” column of the hardware set schedule

      - For two-leaf doors, provide a “top rod only” multi-point lock on both leaves where “(2)” is indicated in the hardware set schedule.

| LOCKSET TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | GRADE 2, CYLINDRICAL LOCKSET | 626 (NON-RATED),652 (RATED) |
| A | GRADE 2, CYLINDRICAL LOCKSET, ELECTRIFIED W/ LATCH RETRACTION, PROVIDE ELECTRIC POWER TRANSFER | 626 (NON-RATED),652 (RATED) |
| B | GRADE 1, MORTISE LOCKSET | 626 (NON-RATED),652 (RATED) |
| C | GRADE 1, DEADBOLT | 626 (NON-RATED),652 (RATED) |

    - TRIM, PULLS AND PUSH PLATES

      - Door Pulls and Push Plates:  Comply with BHMA A156.6.

        - Pull Type:  Straight, unless otherwise indicated.

        - Push Plate Type:  Flat, with square corners, unless otherwise indicated.

      - Provide trim in quantities indicated by “(#)” in the hardware set schedule.

| TRIM TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | KICKPLATE, 10”H x LAR, COUNTERSUNK FASTENERS, 4 BEVELED EDGES | 626 |
| A | 8” PULL, “HANDS-FREE” DESIGN. W/ PLATE 6”x16”, COUNTERSUNK FASTENERS, 4 BEVELED EDGES | 626 |
| B | PUSH PLATE 6”x16”, COUNTERSUNK FASTENERS, 4 BEVELED EDGES | 626 |

    - CLOSERS

      - Provide door closer on each exterior door.

      - Provide door closer on each fire-rated and smoke-rated door.

      - Mount on interior side of door unless otherwise noted.

      - Closing force shall be coordinated to meet the requirements of NFPA 80 for fire rated doors, and to meet the requirements of ICC A117.1 and ADA for all doors.

      - For two-leaf doors, provide a closer on both leaves where “(2)” is indicated in the hardware set schedule.

| CLOSER TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | GRADE 1 | ALUM |
| A | GRADE 1 W/ INTEGRAL STOP FEATURE | ALUM |

    - STOPS

      - Gc shall coordinate selection of stops to suit conditions in the field. Also coordinate w/ integral stop option on closer (if applicable).

      - Provide one per leaf.

| STOP TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | DOME STOP | 626 |
| A | WALL STOP | 626 |
| B | CONCEALED OH STOP | 626 |

    - THRESHOLDS

      - Thresholds:  Comply with BHMA A156.21.

        - Provide threshold at each exterior door, unless otherwise indicated.

        - Threshold Surface:  Fluted horizontal grooves across full width.

        - Field cut threshold to profile of frame and width of door sill for tight fit.

        - Provide non-corroding fasteners at exterior locations.

| THRESHOLD TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| X (TYPICAL) | STANDARD ADA SADDLE 5” WIDTH | ALUM |
| A | HEAVY DUTY ADA SADDLE, 5” WIDTH | ALUM |

    - WEATHERSTRIPPING AND GASKETING

      - If blank, provide silencers.

      - For silencers, provide three per leaf for single doors, and two per leaf for pair doors. Coordinate silencer type with frame material.

      - Provide gasketing along full height of both jambs and full length of head.

      - For two-leaf doors, provide astragal or meeting stile type gasketing.

| GASKETING TYPES | DESCRIPTION | FINISH |
| --- | --- | --- |
| BLANK | SILENCERS | GREY |
| X (TYPICAL) | SMOKE GASKETING | 626 / BLACK |
| A | WEATHER GASKETING | 626 |
| B | DOOR SHOE | 626 |

    - FINISHES

      - Finishes:  Provide door hardware of same finish, unless otherwise indicated.

        - ​​​​Finish:  ​​626; satin chromium plated over nickel, with brass or bronze base material (former US equivalent US26D)​​; BHMA A156.18.

        - Exceptions:

          - Where base material metal is specified to be different, provide finish that is an equivalent appearance in accordance with BHMA A156.18.

          - Hinges for Fire-Rated Doors:  Steel base material with painted finish, in compliance with NFPA 80.

          - Hardware for Aluminum Storefront Doors:  Finished to match door panel finish, except at hand contact surfaces provide stainless steel with satin finish, unless otherwise indicated.

  - PART 3  EXECUTION

    - INSTALLATION

      - Install hardware in accordance with manufacturer's instructions and applicable codes, including accessibility standards.

      - Install hardware on fire-rated doors and frames in accordance with applicable codes and NFPA 80.

      - Use templates provided by hardware item manufacturer.

      - Door Hardware Mounting Heights:   Distance from finished floor to center line of hardware item.  ​​

        - For Steel Doors and Frames:  Install in compliance with DHI (LOCS) recommendations.

        - For Wood Doors:  Install in compliance with DHI WDHS.3 recommendations.

        - Mounting heights in compliance with ADA Standards:

          - Locksets:  40-5/16 inch.

          - Push Plates/Pull Bars:  42 inch.

          - Deadlocks (Deadbolts):  ​48 inch​ to highest operable part.

          - Exit Devices:  40-5/16 inch.

          - Door Viewer:  ​43 inch​ at accessible Type A units; standard height ​60 inch​ at accessible Type B units and elsewhere.

      - Set exterior door thresholds with full-width bead of elastomeric sealant at each point of contact with floor providing a continuous weather seal; anchor thresholds with stainless steel countersunk screws.

    - FIELD QUALITY CONTROL

      - Perform field inspection and testing under provisions of Section 01 40 00 - Quality Requirements.

      - Provide an Architectural Hardware Consultant (AHC) to inspect installation and certify that hardware and installation has been furnished and installed in accordance with manufacturer's instructions​​.

    - ADJUSTING

      - Adjust work under provisions of Section ​01 70 00 - Execution and Closeout Requirements​.

      - Adjust hardware for smooth operation:

        - Maximum 5 lb operating force.

        - Secure latching of all non-rated doors, and rated doors with seals without application of closing force other than force of closer device.

        - Hinge closers to avoid conflict with adjacent walls or structures.

      - Adjust gasketing for complete, continuous seal; replace if unable to make complete seal.

    - CLEANING

      - Clean finished hardware in accordance with manufacturer's written instructions after final adjustments have been made.

      - Clean adjacent surfaces soiled by hardware installation.

      - Replace items that cannot be cleaned to manufacturer's level of finish quality at no additional cost.

    - PROTECTION

      - Protect finished Work under provisions of Section 01 70 00 - Execution and Closeout Requirements.

      - Do not permit adjacent work to damage hardware or finish.

    - HARDWARE LEGEND

      - EXT / INT

        - “EXT” indicates an exterior door, “INT” indicates an interior door.

        - Cannot be left blank.

      - RATING

        - Blank indicates no fire rating.

        - If there is a fire rating, indicate the rating in minutes (e.g., 20, 45, 60 etc.).

      - SGL / PRS / PRB

        - “SGL” indicates a single leaf

        - “PRS” indicates a pair with single leaf active

        - “PRB” indicates a pair with both leaves active

        - Cannot be left blank.

      - EAC

        - This is either “X” or blank.

        - X indicates there is EAC in the hardware set.

        - The specifics are defined elsewhere.

      - HINGES

        - “X” indicates typical hardware.

        - A letter (A, B, C, etc.) indicates different than typical hardware.

        - The specifics are defined elsewhere.

      - CLOSERS

        - Blank indicates no closer.

        - A letter (A, B, C, etc.) indicates a closer is included.

        - A number after a letter in parentheses indicates the quantity of that item.

        - The specifics are defined elsewhere.

      - LOCKSETS

        - Blank indicates no lockset.

        - “X” indicates typical hardware.

        - A letter (A, B, C, etc.) indicates different than typical hardware.

        - The specifics are defined elsewhere.

      - PANIC/EXIT

        - Blank indicates no panic/exit device.

        - A letter (A, B, C, etc.) indicates a panic/exit device is included.

        - A number after a letter in parentheses indicates the quantity of that item.

        - The specifics are defined elsewhere.

      - STOPS

        - “X” indicates typical hardware.

        - A letter (A, B, C, etc.) indicates different than typical hardware.

        - The specifics are defined elsewhere.

      - GASKETING

        - Blank indicates no gasketing (provide typical silencers instead).

        - A letter (A, B, C, etc.) indicates different than typical hardware.

        - The specifics are defined elsewhere.

        - Multiple letters may be used.

      - TRIM

        - Blank indicates no trim.

        - A letter (A, B, C, etc.) indicates a trim is included.

        - Multiple letters may be used if there are multiple trim products in the same set.

        - A number after a letter in parentheses indicates the quantity of that item.

        - The specifics are defined elsewhere.

        - Multiple letters may be used.

      - AUXILIARY

        - Blank indicates no auxiliary hardware.

        - A letter (A, B, C, etc.) indicates auxiliary hardware is included.

        - A number after a letter in parentheses indicates the quantity of that item.

        - Multiple letters may be used if there are multiple trim products in the same set.

        - The specifics are defined elsewhere.

        - Multiple letters may be used.

      - THRESHOLD

        - Blank indicates no threshold.

        - A letter (A, B, C, etc.) indicates a threshold is included.

        - The specifics are defined elsewhere.

    - SCHEDULE

      - See hardware schedule following this Section.